ARCH 348

Building and Environmental Systems in Architecture

LECTURE NOTES

CHAPTER 2

COLD WATER SUPPLY

Water Supply

- Water Authorities’ mains

- Private Sources (Streams, Rivers, Lakes, Wells,

Springs)

The water used must be colourless, free from suspended matter and harmful bacteria, pleasant to taste and for health reasons moderately ‘hard’.

| Wholesome | - Spring water. - Deep well water. | Very palatable |
| --- | --- | --- |
|  | 3. Uplands surface water. | Moderately palatable |
| Suspicious | 4. Stored rain water. |  |
|  | 5. Surface water from cultivated lands. | Palatable |
| Dangerous | - River water to which sewage gains access. - Shallow well water. |  |

### Mains Distribution

The main objective in mains distribution is to deliver good quality water to consumers with a reasonable pressure and quantity that meets the demand.

- Water board:  domestic – fully treated.

- Water board:  industrial – partially treated usually chlorinated.

- Large industrial complexes may provide and treat their own supply.

- The following is an example of water treatment for producing high

quality water for homes.

Pump

Sea

Desalination

Plant (e.g. Reverse Osmosis)

Water Supply

### Service Reservoir

Min. 30 m

Ideal range of the head

This is a large water tank sited to give ideal range of static head where possible	(30m-70m) height.

Max. 70 m

Note: 1m head = 9.8 kN/m2

Pressure,

P g h

### Connection to Buildings

Mains

Water meter

Stop cock

Service pit

Water Tank

Distribution Pipe

Service Pipe

Communication Pipe

### Storage Capacity of Tanks

Storage capacity per person for different building types

| Type of Building Storage per person (Liters) |  |
| --- | --- |
| Dwelling houses and flats | 91 |
| Hostels | 91 |
| Hotels | 136 |
| Offices without canteens | 37 |
| Offices with canteens | 45 |
| Restaurants | 7 |
| Day Schools | 27 |
| Boarding schools | 91 |
| Nurses homes and medical quarters | 114 |

Volumes of water used by each appliance

| Appliance |  | Volume of Cold water (Liters) |
| --- | --- | --- |
| Wash basin | Hand wash | 5 |
|  | Wash | 10 |
|  | Hair Wash | 20 |
| Shower |  | 40 |
| Bath |  | 110 |
| W.C |  | 10 |
| Washing Machine |  | 150 |
| Sink | Wash up | 15 |
|  | Cleaning | 10 |

#### Example for Determining Storage

Capacity of Water Tanks

  - Example: You are designing a boarding school of 200 students and staff. What should be the volume of the cold water tank?

  - Solution:

From the first table for a boarding school

the	storage	required	is	91	Litres	per	person.

Therefore the total volume required is:

Volume = 91 L/person x 200 persons = 18200 L This is the same as 18.2 m3  or 18.2 Tons of water

(Note: 1 m3 = 1000L)

Hardness takes place above this value

Water Quality

US standards for drinking water

| PARTICLES WITHIN WATER | RECOMMENDED LEVEL |
| --- | --- |
| Aluminum | 0.05-0.2 mg/l |
| Chlorite | 250 mg/l |
| Co lour | 15 co lour unit |
| Copper | 1 mg/l |
| Corrosivity | Non corrosive |
| florid | 0.2 mg/l |
| Small particles | 0.5 mg/l |
| Iron | 0.3 mg/l |
| Manganese | 0.05 mg/l |
| Odor | 3 threshold number |
| Silver | 0.1 mg/l |
| Sulphate | 250 mg/l |
| Total dissolved particles | 500 mg/l |
| Zinc | 5 mg/l |

Scaling

The simple definition of water hardness is the amount of dissolved calcium and magnesium in the water. Hard water is high in dissolved minerals, both calcium and magnesium.

(Difficult to obtain a lather with soap)

    - Two types of hardness:

1.Temporary	2. Permanent

can be removed by boiling the water

can not be removed by boiling the water

Hardness level measured in parts per million (ppm)

### Softening Process

Water softener

Base exchange process:

- Removes both temporary and permanent hardness very efficiently by passing the water through zeolites contained in a cylinder.

The process is as follows:

Sodium Zeolite	+	Calcium Sulphate

(in softener)	(or Carbonate)

(in water)

becomes

Calcium Zeolite	+	Sodium Sulphate (or Carbonate)

(held in softener)	(in solution with the water but harmless)

### Backwash Process

Zeolite tank

Salt tank

Water softener

Back wash:

After a period of use the sodium zeolite is converted into calcium and magnesium zeolite, thus losing its softening power. It is then regenerated by the addition of a strong solution of common salt (sodium cloride). The salt is kept in contact with calcium zeolite for about half an hour, in which time the calcium zeolite is converted back into sodium zeolite.

The process is as follows:

Calcium Zeolite	+	Sodium Chloride

(exhausted sodium)	(common salt)

becomes

Sodium Zeolite	+	Calcium Chloride

(regenerated)	(flushed to drain)

Reverse Osmosis is based on the process of osmosis. Osmosis involves the selective movement of water from one side of a membrane (a plastic film that looks similar to cellophane) to the other. To make the process work, pressure is applied to the contaminated water, forcing water through the membrane; purer water collects on the other side of the membrane.

Keeps away

- Viruses (200 – 4000 times bigger than membrane holes)

- Bacteria (2000 – 10000 times bigger than membrane holes)

### Reverse Osmosis System

### Home RO Systems

RO is probably best known for its use in turning seawater into drinking water. However, it is also effective for treating water quality problems in the home.

RO can reduce the amounts of organics, inorganics, bacteria and particulates

that can be found in contaminated drinking water.

### Larger Scale RO Systems

Level Control Switch

LEVEL CONTROL SWITCH

1

m	m 2

m 2	m 1<  m 2+ m 3

Float

m 1> m 2

m 1

m 3

m 3	Float

Water level

Water

level

N	L

S2

S1	S2

M

S3

Main switc h

S1

Water tank (roof-level)

Electric al circ uit- representation

SYMBOLS

Union

Valve

S3	Check-valve

Float switch

Water tank (ground-level)

Pump

Water Transfer by Level Control

Ball valve

N	L

Bladder

Air (1.5 bar)

Pressure

switch

Water

Electrical Motor

Pump

Pressure Booster Sets: Automatic pump operation for high-pressure water transfer

SYMBOLS

Water tank (roof-level)

Pump

Main switc h

Pressure switc h

Union

Float switc h

Chec k-valve

Float valve

Live	Neutral

Membrane vessel

Points of use

Water tank (ground-level)

Pump

Dwellings:

Water transfer to taps and roof-tanks

by pressure booster sets

SYMBOLS

Pump

Pressure switch Flow switc h

Union

L	N

Membrane vessel

Water tanks (roof-level)

Water tank (ground-level)

Pump

Multi-Story Buildings: Water transfer to roof-level tanks by pressure booster sets

### Using Water Efficiently

In many countries (especially in Cyprus) water is scarce and there is a need for using water rationally. Some examples that offer promise of savings:

- WCs (Flushing capacity varies between 22 litres to 9 litres. When dual flush is used it is possible to flush 4.5 litres if no solids are present in the WCs.)

- Showers (Particularly those delivering a fine spray offer great economy of both water and energy. When compared to baths showers save enormous amount of energy. They also save space and are safer in use.)

- Urinals (Normally flushing is arranged to take place every 20 mins by delivering 5 litres of water. Bowl-type urinals proved to require no flushing (i.e., no water) in order to avoid smells.)

- Sensors (Sensors can be used with taps and urinals so that water is used when there is a need only so that wastes are minimized.)

# CHAPTER 3

HOT WATER SUPPLY

Introduction

- Hot water is required for the comfort of people in

buildings.

- Hot water supply must be adequate in order to meet the

occupants’ demand.

- There are different ways of heating water. Depending on the resources available the technologies used can be:

  - Solar water heaters

  - Gas water heaters

  - Electric water heaters

  - Heat pumps

- On the other hand hot water preparation can be

integrated with central heating systems.

Water Heating System in Houses

AIR VENT

COLD

WATER TANK

HOT WATER

STORAGE TANK

Fuel

(Direct Heating)

HOT AND COLD

WATER USAGE

SERVICE PIPE

Heat Losses from Pipes

HOT WATER

STORAGE TANK

DEAD LEGS

DEAD LEGS:

Connections from the hot water source (or secondary flow) to the taps are known as dead-legs.

AIR VENT

### Dead Legs

  - Dead legs occur in hot water systems where water does not move for a period of time.

  - In central systems there are pipework linking the	central supply

with the draw-off points.

  - Between draw-offs the water in the pipe will cool and the next draw off will involve running the cold water to waste before it reaches the tap, creating dissatisfaction, waste of water and heat.

  - In these systems in order to keep consumption within reasonable limits dead legs of pipework serving hot-water taps are governed to following maximum lengths:

| Pipe diameter | Maximum Length (m) |
| --- | --- |
| 20 mm | 12 m |
| 25 mm | 7.6 m |
| More than 25 mm | 3 m |
| Spray taps | 1 m |

How to Avoid Dead Legs

To avoid dead legs in plumbing systems there are two common approaches;

- Install a secondary return pipe.

Trace heating takes the form of an electrical heating

element run in physical contact along the length of a pipe.

Maintain the water temperature at all times with trace heating.

Dead legs

Estimation of hot-water storage

Code of Practice 342 (Centralized Hot-Water Supply, UK)

| Type of Building | Storage per person (litres) | Type of Building | Storage per person (litres) |
| --- | --- | --- | --- |
| Colleges & Schools: Boarding Day | 23 4.5 | Hospitals: General Infectious Maternity Nurses’ homes | 27 45.5 32 45.5 |
| Dwelling houses | 45.5 |  |  |
| Factories | 4.5 |  |  |
| Flats | 32 | Hostels | 32 |
| Hotels (Average) | 35 | Offices | 4.5 |
|  |  | Sports pavilions | 36 |

By use of the table, a dwelling with 3 occupants will require 45.5 x 3 = 136.5	litres of hot water-storage.

  - Estimation of hot -water storage

If the number of occupants is not known the following table may be used

| APPLIANCE |  | VOLUMES OF HOT WATER (Litres) |
| --- | --- | --- |
| WAS H BASIN | Hand wash Wash Hair wash | 1.5 3 6 |
| SHOWER |  | 13 |
| BATH |  | 70 |
| WASHING MACHINE |  | 70 |
| SINK |  | 15 5 |
|  | Wash up Cleaning |  |

### Storage-Type Electric Water Heater

V E N T

340 mm

H = 700 mm

The following figure shows the typical

dimensions used in Cyprus

I N S U L A T I O N

35 mm

H E A T E R  E L E M E N T

I N L E T P I P E

60 mm

O 470 mm

P I P E

O U T L E T P I P E

#### Storage-Type Gas-Fired Water Heater

2

3

4

1

6

5

Thermostat

- Flue pipe

- Cold water feed

- Hot water outlet

- Burner

- Buffer

### Instantaneous Gas Water Heater

Exhaust pipe

Heat exchanger pipes

Burner

Hot water

Gas

Cold

water

### Instantenous Electrical Water Heater

Solar Water Heating System

Solar Collector Assembly

Source: homepower.com

#### Thermosyphon-Type Solar Water Heater

Cold Water Tank

Air vent pipe

Hot Water Cylinder

Collectors

Cold Water Feed

Circulation of Water by THERMOSIPHON

action

#### Forced Circulation Solar Water Heating

Coil used in

indirect heaters

Source;     http://www.pacificenergysales.com/for-homeowners/solar

#### Solar Collectors Integrated into the

Inclined Roof Structure

AIR VENT

INCLINED ROOF

HOT ATER

COLD WATER

TANK	SOLAR

ENERGY

Cold feed

Hot water

W

TANK

SOLAR COLLECTORS

#### Hot Water Generation with Central Boiler

- Hot water can be generated by the central boiler plant and stored

Central heating Boiler

Indirect heating

Hot Water

Cylinder

To radiotors, fan convectors or floor heating

Solar Collectors

Fuel

Pump

Return Flow

Photovoltaic

panels

#### Hot Water Generation with Heat Pumps

Cool air

Warm air

# CHAPTER 4

PIPES

History

Materials:

- Lead used to be very popular material due to its availability, durability and ease of working. It had environmental problems

- Industrial developments have produced a range

of new materials.

- These materials, such as cast iron, copper, wrought iron, steel, plastic and stainless steel, have come into widespread use

Copper as a Pipe Material

Copper:

- Uses: Cold-water service pipes below ground, all cold- and hot-water supply pipework, heating system pipework, particularly in small buildings, and waste pipes.

- Merits: Extremely durable, strong, resistant to mechanical damage, easily worked, good flow characteristics.

- Jointing: Welding or by capillary or

compression joints.

Parts Required for Assembling Copper

Pipes

Copper pipe-fittings

Copper male adapter

Reducing Tee

Brass female adapter

Tee

Brass female elbow

Elbow

Reducing Tee

Joining Copper Pipes

Soldering a copper pipe

Source: https://www.familyhandyman.com/plumbing/how-to-solder- copper-pipe/view-all

Installation of copper pipes

Bonding

By soldering

Capillary solder joints have a very neat appearence. Solder is either applied or is contained in the fitting and when heated by blowlamp spreads through the joint by capillary attraction

Installation of copper pipes

- Compression fitting	• Capillary fitting

water

Steel pipe:

  - Uses: Hot water, heating and chilled installations are the principal uses, but steel pipes are also used in cold-water distribution and waste pipework.

  - Merits: Steel is cheap, very strong, both for water pressure and in resisting damage. Corrosion may be a problem so it should always be galvanized

  - Jointing: Screwed, welding or flanged.

Parts Required for Assembling

Galvanized Steel Pipes

- Union

Galvanized steel fittings

Cap

Nipple

45o Elbow

Plug

Tee

Cross

Opening Threads on Galvanized Steel

Pipes

Galvanized steel pipes

For galvanized steel pipes jointing is by screwed joints.

screwed joint for steel tubing

### Assembled Fittings and Pipe

Union

Teflon thread sealing tape

Gate

valve

Gate Valve

| No | Part | MATERIAL |
| --- | --- | --- |
| 1 | Nut | Mild steel / S. S. |
| 2 | Washer | M. S. / S. S. /Almunium |
| 3 | Hand wheel | Cast Iron / Aluminium |
| 4 | Stem | Brass |
| 5 | Gland nut | Brass |
| 6 | Gland | Brass |
| 7 | Packing | Asbestos rope |
| 8 | Bonnet | Bronze |
| 9 | Check nut | Brass |
| 10 | Wegde | Bronze |
| 11 | Body | Bronze |

Globe valve

| No. | PART | MATERIAL |
| --- | --- | --- |
| 1 | Nut | Mild steel / S. S. |
| 2 | Washer | M. S. / S. S. /Almunium |
| 3 | Hand wheel | Cast Iron / Aluminium |
| 4 | Stem | Brass |
| 5 | Gland nut | Brass |
| 6 | Gland | Brass |
| 7 | Packing | Asbestos rope |
| 8 | Bonnet | Bronze |
| 9 | Disc | Bronze / Neoprene rubber |
| 10 | Body | Bronze |

Steel Pipes

Large diameter pipes can also be obtained with flanges, which facilitate bolting together, to valves and flanged fittings.

Flanged fittings

Butt welding fittings

### Pipes Made of Plastics

Plastic pipe:

  - Uses: Hot water, heating and chilled water installations are the principal uses, but steel pipes are also used in cold-water distribution and waste pipework.

  - Merits: Generally light, easily worked, frost resistant, economical. Some types degrade in sunlight and several types elongate under temperature differences

  - Jointing: gluing, push-fit, solvent weld joint.

Different Materials Plastic Pipes Made Of

PB-1 (Polybutylene) pipes	PP (Polypropylene) pipes

PE (Polyethylene) pipes	Chlorinted Poly Vinyl

Chloride (CPVC) pipes

Poly Vinyl Chloride

(PVC) pipes

Gluing together with adhesive in Chlorinted

Poly Vinyl Chloride (CPVC) Pipes

Jointing and Installation of CPVC pipes

Push-Fit Connection Fittings in Plastic Pipes

- Push-fit connection

Fusion Welding in Plastic Pipes

polypropylene (PP-R) pipes

### PVC Drainage Pipes

Drainage pipes

PVC drainage

pipes

Access for cleaning

Main

Pipe

Cement pipe

Installation of Rainwater and Waste Water

Pipes

Rainwater and sewage systems are not mixed.

### A Landscape Application

CHAPTER 5

SANITARY FITMENTS AND PIPING IN BUILDINGS

Prof. Dr. Uğur Atikol

Sanitary Fitments

Grouped in two categories:

    - Ablution fitments

      - Wash basins

      - Bath tubs

      - Shower trays

      - Kitchen sinks

    - Soil fitments

      - Water closets

      - Urinals

Assembling the Wash Basin

Wash basin

Tap or mixer valve

Overflow

Wall

Cock valve

Cold or hot water supply pipe

15mm or 1/2 inch diameter

Flexible connection

Waste water

In Summary:

Taps or mixers can be either fitted on the walls or on the wash basins

A mixer valve is used

when hot and cold water is available

The object of a water

(or running) trap is to avoid bad odours from the sewer

Flexible connections

are used to connect the taps or mixers to water supply pipes

Running trap

discharge pipe

50mm or 2 inches diameter

Cock valves are used

to cut off the water for repair and maintenance work.

### How Running Trap Works

Rubber seal

32 mm pipe

Bottle-running trap

Trapped water

Waste water discharge pipe (32 or

50 mm)

Nasty odours from the sewer

### Wash Basin Drain P-Trap

Source:

https://theplumbinginfo.com/plumbing-traps/

Dimensions in mm

Source: http://kitchenbathroomfixtures.com/sanliv- bathroom-sink-or-wash-basin-p-trap.html

### Wash Basin Installation Dimensions

Dimensions in mm

Basin Mixer Dimensions

Single-trunk basin-mixer

Dimensions in mm

Source: http://www.plumbware.co.uk/product/mono- basin-mixer-tap/

### Assembling the Bathtub

Source: http://www.diynetwork.com/how-to/rooms-and-spaces/bathroom/the-anatomy-of-a-bathtub- and-how-to-install-a-replacement

### Various Bathroom fitments

Source: F. Hall, Building Services and Equipment, Longman, 1992

Wall-mounted Bath Mixer Dimensions

Dimensions in mm

Source: https://www.dkhoi.com/standard-size-bathtub-measurements/amazing-standard-size- bathtub-measurements-8-size-4.jpg/

Source: F. Hall, Building Services and Equipment, Longman, 1992

### Water Closet

Dimensions L or H are taken into account during discharge pipe installation

Typical dimensions in mm

The design of sanitary pipework systems:

A sanitary pipework system should contain the minimum amount of pipework necessary to carry away the foul water from the building quickly and quietly. It should not create a nuisance or risk to health, nor damage to the fabric, but it must prevent air from the drain or sewer from entering the building under all circumtances.

Traps and discharge pipes to sanitary appliances:

Every sanitary appliance should be fitted with a trap either as an integral part of the appliance or attached to and immediately beneath its outlet. All traps should be accessible and provided with adequate means of cleaning and for this purpose there is an advantage in providing traps which are capable of being readily removed or dismantled.

The minimum internal diameters of traps to various appliances are as follows:

| Domestic Appliance | Minimum Installation dia. |
| --- | --- |
| Wash Basin | 32 mm (1 ¼”) |
| Bidet | 32 mm (1 ¼”) |
| Sink | 40 mm(1 ½ ”) |
| Bath/shower tray | 40 mm(1 ½ ”) |
| Wash Tub | 50 mm (2”) |

Partially evacuated space

Slope: 20mm/m

Max. length 1.70 meters

An air pocket forms between the water attempting to remain in the trap and the waste water flowing towards the stack. The static pressure of this air is below athmospheric pressure, and the water in the trap is pushed away from the trap, leaving an inadequate or non-existent seal. (also noise is created!) The problem is avoided by using 32 mm pipes only when the length is restricted to 1.70 m at a slope of 20 mm/m run.

### Flow in Waste Pipes

The sloping waste-pipe can be up to 3 m long if its diameter is raised to 50 mm. This allows aeration from the stack along the top of the sloping section.

If the waste pipes are longer than 3 m with bends and even vertical parts, they are added a 25 mm open vent pipe as shown above.

#### Vent Pipes for Basins Remotely Located

from the Stack

Trap ventilation pipe

Trap ventilation pipe

Vent pipe Stack

When the sanitary appliances can not be located close to the single stack system, then extra vertical vent pipes should be used.From these vertical vent pipes branches are connected to the end of the traps to ensure proper ventilation of the traps and protect the trap seal.

Source: Peter Burberry, Environment an Services, 8th Ed.1999, Longman

### Washing Machine Connection

45 cm min

to

75 cm max. (some areas)

15 cm min

to

45 cm max.

Source: https://www.pinterest.com/pin/265008759295445602/

f  I

J  I

I

,/ I

, I

l !	-------

I \

I	I

- ---·-·-·······- . --·--····- .

_.._       - -·· --··.. .,.. ......._ ,,    ---

--·---- -·-···--··- -·· -

---

..--·-...·•·  .. ....

·-·--- . ··--·-··-------..·----- ...... . --··-·- .,... .

.-··- -··- .. . -·.. . . . ·-··--··-_...,___

-	i

, . 1	-,venh l C\hrl3----f:l.t:J:J_e_ _JJ?._ ...

1

;	'	_	' a.

105p"1 ev

. -- ·.......----	····--	- - . - ···-- ---·-·---- ·· -·---·-

/	1/	wa .s. h1·A5

-	'	rn- 0:c-h-f·rre- -c-S<2 - ·

c.oY')    ne c-R,v--_n	_

--	-

"-----------···- ·-·

J ,,	-· -

Rough plumbing for a DWV system

WASTE WATER DRAINAGE

Tub

1':" Wane

& Vent

...._..,

Basic Layouts

1 - waste

Branche:;

-& Kltc­

aect te a.ct

·-TO"I FT

·-OATtf"U0

i-WA!=::HRASIN 1·<:TCHEN 51  K

1-A.UTO  WA.S-i; R

1	1

2

3- Rool  •

2

1 " -1XT U : UNIT5

3" Soil VttH

,.7. Was:e Branch

Kltdtert "MIDtael

............. ...,, .

Kltc.heri  lllt•lftOlM

- .'lJ<T >< TuB

i·K TC11EN SINK

3

How the Gene"a plumbline/	mark •1.C•m work•

,	-

/ . \

I

z.01cETS Z·\,''A5:""13A$lf'• S

8

F 1XT;J  C:

UNITS

Glossary

SOIL VENT PIPE A vertical wide pipe into which toilet and other waste appliances discharge which is ventilated at its upper end to prevent syphonage.

INSPECTION CHAMBER Another term for a manhole located over an underground drainage installation to allow access for cleaning and other maintenance.

DRAIN	Underground system of piping to discharge water and sewage away from the building.

WASTE PIPE	A pipe to carry water away from a basin, bath or sink. GULLEY	A fitting of the underground surface water or waste water drain over which downpipes or other above ground drainage discharge.	There are various types e.g. open gulley, back inlet gulley.

# CHAPTER 6

## SANITARY SYSTEMS AND SEWAGE TREATMENT

Sanitary Pipework Systems

Grease seperator

Kitchen

50

Service pit

70

Soakaway

100

Service pits

or manholes

Grease Separator or Grease Trap

Cross-sectional view of the typical construction of grease trap

Lid

Greasy waste water in

Inlet pipe

Layers of Grease

Partition

Less greasy waste water out

Outlet pipe

### Commercial Type Grease Trap

Diffuser Baffle

Upward flow of grease

Grease retention area

Air intake

Flow control

device

Baffle design helps the grease separate from the water

Source: https://www.drain-net.com/shop-by-product/plastic-grease-traps/product/plastic-grease-trap-25-gpm

### Inspection Chambers and Manholes

Source: F. Hall, Building Services and Equipment, Longman, 1992

### Back-drop Pipe

#### Building a Manhole with Backdrop Pipes

Cleaning access

PVC pipe backdrop

Low-level sewer

### Sewage Water

- Sewage is waste water that are discharged from toilets, wash basins, sinks, showers, industrial processes etc.

- The waste water from residences are primarily feces and urine.

Sewage Treatment

Septic Tank

- Septic Tank is a small scale sewage treatment system common in areas with no connection to main sewerage pipes provided by private corporations or local governments.

- The term "septic" refers to the anaerobic bacterial environment that develops in the tank and which decomposes or mineralizes the waste discharged into the tank.

Two-compartment Septic Tank

Soakaway or Seepage Pits

Biological Treatment Plants

Compressor

Primary settlement chamber	Aeration chamber

Final settlement zone

(Micro-organisms developed through bubble generation)

### Separating Rainwater from Sewage

### City Scale Sewage Treatment Plants

In many cities the waste water is carried to central sewage treatment plants by means of pipes. The contaminants are removed and the cleaned water is either used in irrigation of plants or discharged into the rivers or lakes.

CHAPTER 7

VENTILATION

- Why do we need to do ventilaton in buildings?

  - The main reason is to decrease the humidity in a given environment and improve the air quality. Ventilation is also practiced in places where the “bad” air is needed to be replaced by fresh air.

Respiration

Wet air

Dry air

Kitchen	Bathroom

- Problems associated with poor air quality

  - Healt effects

    - Headaches

    - Sore throat

    - Respiration problems

    - Stinging eyes

    - Tiredness

    - Allergies

  - Dustmites

  - Radon

  - Moisture

  - Damp stains

  - Mould

  - REDUCTION IN HUMIDITY LEVELSS

-Dust-mite levels decrease

-Mould disappears

-Fungus disappears

  - REMOVES THE CAUSE OF TIREDNESS AND HEADACHES

-High CO² levels are replaced with fresh air

-Moist, stuffy air is eliminated

-Poisonous particles emitted by artificial building materials are removed

  - ELIMINATES RADON PROBLEMS

-Radon gas will be ventilated away

  - REDUCES THE NEED FOR REDECORATION

-Cigarette smoke will not linger

-The amount of pollution in the air decreases

  - LOWERS THE HEATING COST

-A damp house is impossible to heat (try heating a wet towel)

- Kitchens

- Bathrooms

- Restaurants

- Conference rooms

- Theatre buildings

- Places where people smoke

Humidity increases

as we use the shower and the kitchen

Kitchen	Bathroom

Ventilation and Heating

Ventilation is essential for a fresh, comfortable atmosphere. With the introduction of central heating, insulation and draught proofing, well designed ventilation becomes vital.

Without a constant change of air, centrally heated rooms quickly become stuffy and before long the moisture content of the air becomes so high that water is deposited as condensation.

There are various ways to provide ventilation, some extremely simple, others much more sophisticated for total control.

Natural ventilation	Mechanical ventilation

Natural Ventilation

Stack-effect Ventilation

Winds from leeward creates a suction

Cross- ventilation

Fresh air entering through a widow

Fresh air entering through a widow

Stack-effect ventilation in commercial buildings

Example design of stack ventilation

Stack ventillation design in the building of British High Commission in Colombia

Mechanical Ventilation

Exhaust air

Fresh air

Exhaust fan

### Mechanical Ventilation

Exhaust air

Fresh air

### Choosing the Fan Size

The size of a fan, or to be more accurate its capacity is determined by the type of room in which it is installed and the volume of air it must move.

A fan installed in a kitchen must be able to change the air completely 10 – 15 times per hour. Other types of rooms have different standards:

| Room | Air changes per hour |
| --- | --- |
| Bathroom | 15 – 20 |
| WC | 10 – 15 |
| Living room | 4 – 6 |

Example: A kitchen has a length of 3.35m, width 3.05m, hight of 2.44m. Calculate the fan capacity to be appropriate for this kitchen.

Volume=3.35 x 3.05 x 2.44 = 24.93 m3

Air changes per hour can be taken to be 15. Fan capacity = 24.93 x 15 = 374 m3/hour.

Note: In ducted applications pressure losses need to be estimated as well.

### Ducted Ventilation Systems

Kitchen Equipment

### Conditioning with Ventilation

Rooftop unit

Fresh air

Mixing chamber

Roof A/C

Supply air

Roof

Return air

Exhaust

air

Conditioned Building

Efficiency in Winter

5oC

Indoors

20oC

8oC

Outdoors

17oC

(Source: http://omega-bud.pl/main.php?l=en&p=l)

Efficiency in Summer

35oC

Indoors

24oC

38oC

Outdoors

27oC

(Source: http://omega-bud.pl/main.php?l=en&p=l)

Heat Recovery Ventilation

Demand Control Ventilation

Demand Controlled Ventilation for Energy Efficiency

  - What is it?

    - Vary outdoor air intake (fresh air) to match current occupancy

  - How can it be done?

    - Time-of-day schedules

    - Occupancy (on-off) sensors

    - CO2-based L/s per person sensing

      - Measure CO2 in return ducts, and keep levels under approximately 1000 PPM

Variable Speed Drives (VSDs) are required

Air duct

Motor

VSD

Fan

Air flow

Electricity

input

Feedback signal from

occupancy sensor (or other sensors) is sent to VSD to increase or decrease the speed of motor

Variable Speed Drives for Energy Efficiency in Fans Applications

- Because of the fan laws, large savings can be achieved using variable speed drives for fans and pumps. The cube law says:



kW	RPM	3

new

	new

kWold

RPM

3

old

- Example: If fan speed is reduced by a half, the power consumed is reduced by 1/8.

CHAPTER 8

CENTRAL HEATING

Central Heating

- A central-heating system provides warmth to the whole interior of a building (or portion of a building) from one point to multiple rooms.

- Central heating can be achieved by

  - Combustion of fosil fuel by a furnace (boiler)

70oC

Boiler

90oC

Room 4

Room 1

Room 3

Room 2

Air-to-air heat pump system

  - Air-to-water heat pumpsystem

  - Water-to-water heat pump system

  - Solar thermal systems.

- Heat is distributed by

  - Water circulating through pipes

  - Forced air through ductwork

  - Steam circulating through pipes

Hot water central heating system

### Components

- Boilers (or heat pumps)

- Solar collectors

- Heat distribution pipes or headers

- Hot water tanks

- Underfloor pipes

- Radiators

- Towel rails

- Fan convectors

(Source: http://www.centralheating.co.nz/net/learn/how-it-works.aspx)

### One-pipe Central Heating System

Radiator thermostat

Room thermostat

Central Heating with Boilers

Central heating Boiler

Efficiency = 0.83 – 0.95

To radiotors, fan convectors or floor heating

Return pipe

Fuel	Flow pipe

Pump

Burner

Hydro-flow (or water circulation) Heating Systems

Combi-boiler

Radiators

Shower

Tw o-pipe system

With flow and return pipes.

(http://www.centralheating.co.nz/net/learn/how-it-works.aspx)

Cast iron block

Burner

Can be gas or oil fired

FLAME

Bedroom

Corridor

Radiators and Towel Rails

Bathroom

Why place them under the windows?

Radiator placed on an interior wall	Radiator placed under the window

Source: http://www.bestheating.com/info/blog/how-does-a-radiator-heat-the-room/

A cutaway of underfloor heating arrangement

Floor finish

Pipework

Screed

Thermal insulation

Slab

Radiator heating	Underfloor heating

Source: https://www.incognitoheatco.com/underfloorheating/comfort/

Radiator Heating	Underfloor Heating

### Heat Pumps

Refrigeration Cycle

Compressor

E.V.

Evaporator

Condenser

(http://www.samsainc.com/refrigeration.html)

(http://www.descoenergy.com/system_type.htm)

Coefficient of Performance = 3 – 5 (in warm climates)

Ducted Packaged Systems or Rooftop Units

Rooftop Unit with Fresh Air

Rooftop unit

Fresh air

Mixing chamber

Roof A/C

Supply air

Roof

Return air

Exhaust

air

Conditioned Building

Heat Recovery Ventilation

Heat recovery ventilation for Energy Efficiency in Winter

5oC

Indoors

20oC

8oC

Outdoors

17oC

(Source: http://omega-bud.pl/main.php?l=en&p=l)

### Air-to-Air Split System Heat Pump

Heat

Cooled

air

Heat is absorbed by the refrigerant leading to its evaporation

Heat from air

Heat

Heat

Refrigerant releases its heat and condenses

Electricity to compressor

#### Ducted Split-Unit Heat Pump Systems

Ducting

Supply grilles

Outdoor unit	Indoor unit

Air-to-Water Heat Pumps

Evaporator coils

Cool air

Warm air

Condenser coils

The achieved water temperatures are most appropriate for underfloor heating

Variable Speed Drive (VSD) in Ducted Systems

Air duct

Motor

VSD

Fan

Air flow

Pressure

sensor

Electricit

y input

Feedback signal is

sent to VSD to increase or decrease

the speed of motor

### Variable Speed Drive (VSD)

###### Because of the fan laws, large savings can be achieved using variable speed drives for fans and pumps. The cube law says:



kW	RPM	3

new

	new

kWold

RPM

3

old

###### VSD can be applied to all electric motors (where ever they are available in a system) in order to achieve energy efficiency.

Fans, pumps, compressors etc.

CHAPTER 9

MECHANICAL COOLING

Central Cooling

- A central-cooling system provides coolness to the whole interior of a building (or portion of a building) from one point to multiple rooms.

- Central cooling can be achieved by

  - Single package refrigeration units using water as energy carriers (i.e. Chillers)

  - Single package ducted refrigeration units

  - Split unit ducted refrigeration units

  - Air-to-air heat pump system

  - Air-to-water heat pump system

  - Water-to-water heat pump system

  - Evaporative coolers

  - Absorption refrigeration units

- Heat is distributed by

13oC

Room 4

Chiller

7oC

Room 1

  - Water circulating through pipes

  - Forced air through ductwork

Room 3

Room 2

Chilled water central

heating system

### Evaporative Cooling

#### Vapor Compression Refrigeration Cycle

Compressor

Heat is absorbed from the cooled environment

Evaporator

E.V.

Condenser

Heat is released to a nearby environment

Coefficient of Performance = 2.5 – 3.5 (in warm climates)

(Source: http://www.samsainc.com/refrigeration.html)

### Chilled Water Cooling System

Fan Coil Units

FCU-1	FCU-2	FCU-3

Air handling unit

AHU

Flow

Duct

Pump

Return

Cool Air

Flow water ~ 7 deg C Return water ~ 13 deg C

Fan Coil Unit (FCU)

Fans

Coil

Typical FCU Connection

3-way valve

Room Thermostat

Flow

Return

3-way valve

Condensate tray

Fan

Source: https://www.pinterest.com/pin/211528513731818584/

##### System Improvement Options for Energy Efficiency

###### Make building envelope improvements to reduce cooling load

insulation, high performance windows and roofs

Replace old cooling units and chillers with more efficient models

Consider multiple chillers

Consider a chiller with a variable speed drive

Ducted Split Unit Systems

Ducting

Outdoor unit

Indoor unit

Refrigerant piping

Variable Refrigerant Volume (VRV)

Expansion valves

Compressor

(Variable speed drive)

Evaporator

Evaporator

Evaporator

Condenser

Atmosphere

### VRV System in Summer Mode

Fans

Warm Air

Flow

Cool Air Flow

Indoor units comprise of:

Outdoor unit comprise of

•

•

•

expansion valve

evaporator (condenser) fan

- condenser (evaporator)

- compressor

- Fans

#### Water Cooling with Heat Pump Systems

Flow to fan-coils

Return from fan-coils

Expansion valve

Heat

Condenser

Heat

AGtrmouonsdphoerre Water reservoir

Evaporator

Energy storage:

Water tank

Compressor

### Packaged Rooftop Unit

Cooling coil

Fan

Condenser

Fresh air intake

Compressor

Supply air duct

Return air duct

### Rooftop Unit with Fresh Air

Rooftop unit

Fresh air

Mixing chamber

Roof A/C

Supply air

Roof

Return air

Exhaust

air

Conditioned Building

Duct Configurations

Plans of an Amphi-theatre

with the application of roof-top a/c

E.F.

Roof-top unit

Roof top unit

Fresh air intake

Duct